## Survey
Denver Fire Dept. ERCES RF Survey v2025 CONFIDENTIALITY NOTICE: This document is intended solely for the purpose of documenting ERCES within the City and County of Denver and may contain information that is confidential, legally privileged, and/or exempt from disclosure under applicable law. You are hereby notified that any unauthorized review, forwarding, printing, copying, distribution, or use of this document or the information it contains is strictly prohibited.
Date
New Install/Maintenance/Repair
Permit Number
Associated permit numbers
Building Name
Building Address
After Hours Contact Info (for service calls)
Total Number of Floors
Number Below Ground Levels
Floors With Service Antennas
Square Footage of Each Floor
Company / DFD License Number
Number of active equipment | Remote 1 | Remote 2
BDA Manufacturer
BDA Model
BDA band configuration
BDA S/N
FCC Booster ID #
BDA Location (floor/room)
BDA Firmware Version
Downlink Gain
Downlink ALC or AGC setting
Uplink Gain
Uplink ALC or AGC setting
Uplink Squelch Threshold
UPS/BBU Model #
Battery Model
Calculated Back-Up Time
Donor Antenna Manufacture/Model
Donor Antenna Gain
Donor Antenna Pointed at which Site?
Donor Antenna Azimuth
Distance from Site
External Band-Pass Filter Make/Model/Band
Fixed Attenuator? (value/location)
Control Channel RSSI (measured w/o attenuation)
DL Composite input power (w/o attenuation)
Estimated near/far channel power at site
Estimated noise level at site
Measured Antenna Isolation
Dedicated labeled electrical circuit # w/ lockout
Uplink Amplifier should remain off until inspection
Caution! When performing Isolation Test, Never transmit over Donor Antenna
BDA installer required to provide screen shots of Donor antenna FREQ RL, DTF RL, and BDA UL noise pedestal.
Notes:
Note on A4: Current active permit number
Note on A5: List any additional permits that may be related to this RES
Note on A14: Document any additional equipment related to the RES including the BDA, remotes or fiber units. If there are more than 2 remotes add a new column
Note on A16: List the full model or part number of the BDA
Note on A17: Internal filtering (Class A or B) and band pass info
Note on A19: All BDA's must be registered with FCC
Note on A21: Document the current firmware version
Note on A23: Document the AGC/ALC/Target value for the Downlink. Provide both composite and per filter
Note on A25: Document the AGC/ALC/Target value for the Uplink, provide both composite and per filter
Note on A30: As of 2025, Donor antenna horizontal beamwidth shall be less than 45 degrees
Note on A32: Donor antenna location must be coordinated in advance with DFD Lineshop
Note on A35: Was an external filter installed?
Note on A36: Document attenuation added at Donor or Service ports
Note on A37: Control Channel Measured at Donor port of BDA without attenuation
Note on A38: Measured composite power for 806-816 at donor port
Note on A39: Record near and far signal levels for the RES. *Denver requires and minimum of -100dBm and a maximum of -75dBm for the desired signal delivered to the radio site. *Near far testing can be completed using a signal generator set for a channel within the configured setting of the BDA, a 50ohm load is required at the donor port of the BDA to prevent transmitting over the air.
Note on A40: Document in band noise measured in 10kHz RBW delivered to radio site. *Denver requires noise in band to be 15dB below thermal noise at the site (-149dBm or less)
Note on A41: Denver requires a minimum 20dB isolation over max gain of BDA
Note on A42: (Y / N) Dedicated circuit with lockout at panel, also provide circuit number

## Screen Shots
Please attach required sweeps for each test listed below:
Donor Ant Freq RL (Donor antenna line with Donor antenna attached)
*Freq span of the trace should match the band pass of the in line components
Donor DTF RL (Donor antenna line with 50ohm load)
*Freq span of the trace should match the band pass of the in line components
Measured UL noise pedestal (at configured gain setting with squelch disabled)